## SOW
Client | Saatvik Agro products Morena, MP
Project Capacity AC-KW | 1300
Project Capacity DC KWp | 1695.27
SCOPE OF WORK
|  |  | 815.23 | 498.96 | 444.42 |  |  |  | Scope of Work
S.No. | Item Description | SPECIFICATION | Qty | Qty | Qty | Total | UOM | MAKE | Supply | Service | Rate | Amount
PV Section |  |  | Process P | FMG-1 | Storage
1 | Solar PV module (Wp) | PV Module 405Wp | 220 | 1232 | 874 | 2314 | Nos. | Saatvik | Saatvik | Contractor
2 | Solar PV module (Wp) | PV Module 445Wp | 1474 | 0 | 0 | 1704 | Nos. | Saatvik | Saatvik | Contractor
3 | Solar PV module (Wp) | PV Module 585Wp | 120 | 0 | 120 | 0 | Nos. | Saatvik | Saatvik | Contractor
4 | MC4 Connector | MC4 Male & Female Field side connector (MC4 compatible, IP67) | 362.8 | 246.4 | 198.8 | 609.2 | Lot | Elmex | Contractor | Contractor | 40 | 24368
5 | String Inverter | LT String inverter 50KW | 13 | 8 | 8 | 26 | Nos. | Saatvik | Saatvik | Contractor | 0 | 0
6 | Remote Monitoring system - Web based | Web based Datalogger for minitoring | 1 | 1 | 1 | 3 | Nos. | Suryalogix/Power AMR | Contractor | Contractor | 50000 | 150000
7 | Zero Export devise |  | 1 | 0 | 0 | 1 | Nos. | Suryalogix/Power AMR | Contractor | Contractor | 2500000
8 | Communication Cable | RS485 Armourd shielded cable for communication inverter to inverter | 316 | 250 | 270 | 836 | Mtrs | D-Link/Polycab/Beldan | Contractor | Contractor
9 | DWC Conduit, Size of 32mm OD | Schedule 40 UV Protected | 316 | 250 | 270 | 836 | Mtrs | Supreme/Titupati/Reputed | Contractor | Contractor
10 | L-JOINT PVC 32mm | Schedule 40 UV Protected | 120 | 120 | 120 | 360 | Nos. | Supreme/Titupati/Reputed | Contractor | Contractor
11 | T-JOINT PVC 32mm | Schedule 40 UV Protected | 120 | 120 | 120 | 360 | Nos. | Supreme/Titupati/Reputed | Contractor | Contractor
12 | Weather Monitoring Station (Reference Cell Radiation Sensor) | 1. Radiation sensor. (2 Nos) 2. Temperature Sensor - Ambient (1 Nos) 3. Temperature Sensor - Module (1 Nos) | 1 | 0 | 0 | 1 | Set | Webdyn/Trinity/Suryalogix | Contractor | Contractor
Structures, Walkway Railing & life line
13 | MMS | Standing seam type Al anodized H clamp with hardware & other accessories | 815.23 | 498.96 | 444.42 | 1695.27 | KWp | Reputed make | Contractor | Contractor
14 | Walkway | FRP Walkway 300 width x 25mm | 940 | 795 | 480 | 1610 | RM | Reputed make | Contractor | Contractor
15 | Walway clamps | Mounting clamps & accessries | 1880 | 1590 | 960 | 1 | Lot | Reputed make | Contractor | Contractor
16 | Safety life line | Stainless steel type life line with Standing seam clamp type structre support as per approved drawing | 336 | 270 | 210 | 735 | RM | Reputed make | Contractor | Contractor
17 | Handrail | FRP 800 MM height with mounting arrangement |  |  |  | 250 | RM | Reputed make
DC side - Cables & Accessories
18 | DC Cable (1Cx4mm² (+VE & -ve)) | 1 Core 4 Sqmm Cu 1.5kV , UV protected XLPO Solar Grade Cable - EN 50618 IS-1554 Part-1,Temp range:- 10Deg C to +120Deg C,Voltage range-1.5KV,excellent resistance to heat,cold,water,oil,abrasion,UV radiation, flexible. Life of cable-more then 25 year. Cable should be annealed Hight conduction copper conductor with XLPO insulation,UV protected.XLPO having working voltage- 1500V,UV resistant for outdoor installation IS/IEC 69947,For AC/DC cables Voltage drop= 1% limited | 4484 | 2745 | 2445 | 9674 | Lot | KEI/HAVELLS/APAR/UNIVERSAL/Sichem | Contractor | Contractor
19 | DWC Conduit, Size of 40mm OD | Schedule 40 UV Protected | 1200 | 1200 | 1200 | 3600 | Lot | SUPREME/TIRUPATI/REPUTED | Contractor | Contractor | 21 | 75600
20 | L-JOINT PVC 40mm | Schedule 40 UV Protected | 80 | 80 | 80 | 240 | Lot | SUPREME/TIRUPATI/REPUTED | Contractor | Contractor
21 | T-JOINT PVC 40mm | Schedule 40 UV Protected | 130 | 130 | 130 | 390 | Lot | SUPREME/TIRUPATI/REPUTED | Contractor | Contractor
22 | MISC Items | GI Saddle, Silicon & Accessories | 1 | 1 | 1 | 3 | Lot |  | Contractor | Contractor
AC side - Cables & Accessories
23 | AC Cable (For Inverter to LT PANEL) | 3.5C X 50 sq.mm AL. A. XLPE Cable 1.1kV (For Inverter to LT PANEL) Cable shall be stranded AL. AR. conductor with XLPE insulation, UV protected , 1.1KV, temp range -10ºC to +80ºC overall XLPE insulation for outdoors, FRLS TYPE | 2080 | 1520 | 1280 | 4880 | Lot | POLYCAB/KEI/HAVELLS/APAR/UNIVERSAL/Gems | Contractor | Contractor
24 | AC Cable ( LT PANEL to Existing panel ) | 3.5C X 300 sq.mm AL. A. XLPE Cable 1.1kV (For Inverter to LT PANEL) Cable shall be stranded AL. AR. conductor with XLPE insulation, UV protected , 1.1KV, temp range -10ºC to +80ºC overall XLPE insulation for outdoors, FRLS TYPE | 100 | 50 | 50 | 200 | Lot | POLYCAB/KEI/HAVELLS/APAR/UNIVERSAL/Gems | Contractor | Contractor
25 | Double compression Cable Gland & Accessries | For All types of cable required, | 0 | 0 | 0 | 0 | Lot | Reputed make | Contractor | Contractor
26 | LUGs (Cu, Al, Bi-metalic) | As per requirement | 39 | 21 | 21 | 81 | Lot | Reputed make | Contractor | Contractor
27 | Heat shrinkable sleeve | for all cables | 1 | 1 | 1 | 3 | Lot |  | Contractor | Contractor
28 | LT PANEL (8in-1out) | As per specfification 415V LT Panel : 9 in1-out LT Panel indoor compartment type - 100A 4P MCCB nos input and 800A MCCB output - MFM meter with RS485 commiunication | 2 | 1 | 1 | 4 | Nos. | CUSTOM MADE SWITCHGEAR MAKE - ABB/SIEMENS/L&T/SCHNEIDER | Contractor | Contractor
29 | LT PANEL (6 in-1out) | As per specfification 415V LT Panel : 6 in1-out LT Panel indoor compartment type - 100A 4P MCCB nos input and 800A MCCB output - MFM meter with RS485 commiunication |  |  |  |  | Nos | CUSTOM MADE SWITCHGEAR MAKE - ABB/SIEMENS/L&T/SCHNEIDER
30 | Extension Panel | Extention Panel with 800A MCCB | 2 | 0 | 0 | 2 | Nos. | CUSTOM MADE SWITCHGEAR MAKE - ABB/SIEMENS/L&T/SCHNEIDER | Contractor | Contractor
31 | 1C 16 sq.mm cu flexible (Cable for earthing - Inverter Earthing) | Inverter Earthing & LT Panel | 100 | 100 | 100 | 300 | Lot | Reputed | Contractor | Contractor
32 | 1C x 2.5 Sqmm Cu Cable | Module To module Earthing | 598.62 | 406.56 | 328.02 | 1333.2 | Lot | Reputed | Contractor | Contractor
33 | 1C X 70 Sqmm Cu Cable | LA Earthing | 75 | 50 | 50 | 175 | Lot | Reputed | Contractor | Contractor
Earthing- Cables Lugs - Lumpsum Items | [5 empty] | 0
34 | Earthing Hardware | SS Hardware M4 x 15mm for module earthing | #REF! | #REF! | #REF! | 1 | Lot | Reputed | Contractor | Contractor
35 | Earthing Hardware | M6 x 30 with nut + double washer | 600 | 600 | 600 | 1 | Lot | Reputed | Contractor | Contractor
36 | Earthing Hardware | M8 x 30 with nut + double washer | 100 | 100 | 100 | 1 | Lot | Reputed | Contractor | Contractor
MISCELLANEOUS | [5 empty] | 0
37 | Cable Ties & MC4 Clips | UV Protected Sizes-As per requirement | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
38 | Cable Tray- DC Side | Pre GI Perforated with cover & Fixing accessories. Support angles & stands | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
39 | Cable Tray-AC Side | Pre GILadder type, & Fixing accessories. Support angles & stands | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
40 | Danger Boards & Safety Tags | Building evacuation plan and direction signs, assembly points Signages | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
41 | Fire Fighting System | DCP ABC/POWDER Type - 6 Kg - IS 2171 & IS 10658 Marked | 1 | 1 | 1 | 6 | Nos | Reputed | Contractor | Contractor
42 | Fire Fighting System | CO2 Type - 6 Kg - IS 2171 & IS 10658 Marked | 1 | 1 | 1 | 3 | Nos | Reputed | Contractor | Contractor
43 | Fire Fighting System | SAND BUCKET STAND WITH 3 BUCKET ARRANEGEMNT & COMPLETE ACCESSORIES - 24 SWG - IS 2546 | 1 | 1 | 1 | 3 | Nos | Reputed | Contractor | Contractor
44 | Ferrules & Cable tags | Printed tube type Appropriate Cable Tags ( At all Power & AUX cables Terminal Points Metallic Tags to be provided ) | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
45 | Foam Sealent | Silicon Based - Sealing for conduit openings | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
46 | STICKER & Marking | Equipment marking. Radium Based with Strong Adhesive | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
47 | Electrical Tape | RED, YELLOW, BLUE, BLACK, GREEN ( Each 5) | 1 | 1 | 1 | 1 | Lot | Reputed | Contractor | Contractor
48 | Inverter Stand with Canopy | As per approved drawing | 13 | 8 | 8 | 26 | Nos. | Reputed | Contractor | Contractor
49 | Insualtion Mat | As per IS & 1.1 KV Voltage grade. Insualtion rubber mats 1 meter x 2 meter | 4 | 4 | 4 | 1 | Lot | Reputed | Contractor | Contractor
EARTHING & LIGHTNING PROTECTION | [5 empty] | 0
50 | Earthing | GI Strip 25X3 mm | 1300 | 1300 | 1300 | 1 | Lot | Reputed | Contractor | Contractor
51 | Earthing | GI Strip 25X6 mm | 1300 | 1300 | 1300 | 1 | Lot | Reputed | Contractor | Contractor
52 | Earthing | Chemical Earthing Pit As Per IS 3043, - ARRAY YARD EARTHING & A) 17.2 MM Dia, 3 MTS Height Cu Coated(250 Microns) Steel Rod, T Joints For Earth Strip Connection B) Chemical Earthing Backfill Compound, 22.5 Kg C) Pre Cast RCC Chamber Adhension/Bending/Environment test/UL Approved/Cu purity test, Micron Coating for Earth Electrode Ph Value, Leaching test, Resistivity test & Strength test for backfill chemical | 15 | 10 | 15 | 32 | Set | SABOO/VNT/true Power | Contractor | Contractor
53 | Red insulator with hardware | Size-40MM which to joint with roof sheet with fixing clamps | 100 |  |  | 1 | Lot | Reputed | Contractor | Contractor
54 | Lighting Arrestor as per IEC -68-2-52 Part 2,.ESE Type NFC17-102(2011) with Strike counters | Lighting Rods with 5Mtr Length Level 3 with accessories(GI mast, stray wire with fixing accessories) Insulators & Accessories for earth strip - Plastic/Ceramic - 50 MM Width - With suitable mounting arrangement (For Roof mounted & LA) | 1 | 1 | 1 | 3 | Nos. | SABOO/VNT/true Power | Contractor | Contractor
Module cleaning System | [5 empty] | 0
55 | MCS | Manual Module cleaning system with UPVC piping network and 3 Nos Booster pump & Brass nozzles. Hose Pipe-100 Mtr for each bulding, Wiper Incl. Electrical connection & Canopy | 815.23 | 498.96 | 444.42 | 1 | Lot | ASTRAL/APL APOLLO/DURALINE/SUPREME/TIRUPATI/REPUTED | Contractor | Contractor
I&C | [5 empty] | 0
56 | LT Panel foundation | - LT panel foundation as per approved drawing | 2 | 1 | 1 | 4 | No | REPUTED | Contractor | Contractor
57 | Earthing pit chamber | - Earthing pit chamber 350mm x 350mm | 15 | 10 | 10 | 35 | Nos | REPUTED | Contractor | Contractor
58 | Electrical & MMS | Installation & testing, pre commissioning of all equipments including cabling, termination, mounting, road cutting,hume pipe installation,housekeeping, white wash of foundation, MS fabrication, suppots, all required fitting, loading, unloading shifting of material, Tools, tackles, equipment, machinery-Hydra, forklift, ladder, water, electricity for construction, paint work,RCC cutting, material reconciliation, testing of equipments, support work for CEIG/Govt. approvals. | 815.23 | 498.96 | 444.42 | 1695.27 | KWp |  | Contractor | Contractor
59 | Consumables | All type of consumables required as per site condition | 1 | 1 | 1 | 1 | Lot | Reputes | Contractor | Contractor
60 | CEIG Approval |  | 815.23 | 498.96 | 444.42 | 1695.27 | KWp |  | Contractor | Contractor
| Net Metering | All Statutory approvals & Metering cubical along with Meter, CT, PT as per discomm Standards |  |  |  | 400 | KW |  | Contractor | Contractor
61 | Safety | All required PPEs/First Ad Kit ISI marked or as per client's requirement, Comply with Client's EHS policy. And Third party inspection of machinery & equipments if required | 1 | 1 | 1 | 1 | Lot |  | Contractor | Contractor
62 | Labor compliance | All required labor compliances like-PF,ESI,WC policy, EAR policy,GPA etc | 1 | 1 | 1 | 1 | Lot |  | Contractor | Contractor
63 | Supply Misc | All Misc Items - C class Items not included in BOQ, support structure, fittings | 1 | 1 | 1 | 3 | Lot |  | Contractor | Contractor
64 | MS Painted Step 2 Mtr each side | With handle for Roof monitoring crossing |  |  |  | 3 | Set |  | Contractor | Contractor
65 | MS Painted sky light protection | with Wire mess and fixing accessories |  |  |  | 1 | Lot |  | Contractor | Contractor
Note :
Above mentioned quantities are on estimate basis, these may vary +/- 10%
Statutory fees shall be reimburse on submission of actual challan/bill
All Material shall be dispatch on the issue of the MDCC By client
Loading & Unloading , shifting of free Issue items shall be in the scope of the contractor
Arrangement of Electricty, water shall be in the scope of the contractor
Any other material requirement for the successful commissiong of the plant which is not mentioned in the above BOQ will be in the scope of the contractor
Completion Time- 60 Days from the date of PO/Advance